## Control
Coil Number | Registers | Description |  |  |  | Signal Direction
1-16 | 50000 | Frequency converter control word (see table below) |  |  |  | Master to slave
17-32 | 50010 | Frequency converter speed or set-point reference Range 0x0 – 0xFFFF (-200% ...~200%) |  |  |  | Master to slave
33-48 | 50200 | Frequency converter status word (see table below) |  |  |  | Slave to master
49-64 | 50210 | Open loop mode: Frequency converter output frequency Closed loop mode: Frequency converter feedback signal |  |  |  | Slave to master
65 |  | Parameter write control (master to slave) |  |  |  | Master to slave
0 = Parameter changes are written to the RAM of the frequency converter
1 = Parameter changes are written to the RAM and EEPROM of the frequency converter.
66-65536 |  | Reserved
Coil | 0 | 1 | Coil | 0 | 1
01 | Preset reference LSB |  | 33 | Control not ready | Control ready
02 | Preset reference MSB |  | 34 | Frequency converter no tready | Frequency converter ready
03 | DC brake | No DC brake | 35 | Coasting stop | Safety closed
04 | Coast stop | No coast stop | 36 | No alarm | Alarm
05 | Quick stop | No quick stop | 37 | Not used | Not used
06 | Freeze freq. | No freeze freq. | 38 | Not used | Not used
07 | Ramp stop | Start | 39 | Not used | Not used
08 | No reset | Reset | 40 | No warning | Warning
09 | No jog | Jog | 41 | Not at reference | At reference
10 | Ramp 1 | Ramp 2 | 42 | Hand mode | Auto mode
11 | Data not valid | Data valid | 43 | Out of freq. range | In frequency range
12 | Relay 1 off | Relay 1 on | 44 | Stopped | Running
13 | Relay 2 off | Relay 2 on | 45 | Not used | Not used
14 | Setup LSB |  | 46 | No voltage warning | Voltage warning
15 | Setup MSB |  | 47 | Not in current limit | Current limit
16 | No reversing | Reversing | 48 | No thermal warning | Thermal warning
Frequency converter control word (FC profile) |  |  | Frequency converter status word (FC profile)
Can also be controlled using registers
50000 Input data: Frequency converter control word register (CTW). |  |  |  | ex: 047C hex = Start / 043C hex = Ramp stop
50010 Input data: Bus reference register (REF). |  |  |  | 100% = 4000 hex / 16384 dec
... ...
50200 Output data: Frequency converter status word register (STW).
50210 Output data: Frequency converter main actual value register (MAV).

## Data readout
Parameter Number | Parameter Name | 4X Registers in DEC | Registers in HEX | Data type | Conversion index
1600 | Control Word | 16000 | 3E80 | V2 | 0 | Data type | Description
1601 | Reference [Unit] | 16010 | 3E8A | Int32 | -3 | Int8 | Integer 8
1602 | Reference [%] | 16020 | 3E94 | Int16 | -1 | Int16 | Integer 16
1603 | Status Word | 16030 | 3E9E | V2 | 0 | Int32 | Integer 32
1605 | Main Actual Value [%] | 16050 | 3EB2 | N2 | -2 | Uint8 | Unsigned 8
1609 | Custom Readout | 16090 | 3EDA | Int32 | -2 | Uint16 | Unsigned 16
1610 | Input Power [kW] | 16100 | 3EE4 | Int32 | 1 | Uint32 | Unsigned 32
1611 | Input Power [hp] | 16110 | 3EEE | Int32 | -2 | VisStr | Visible String
1612 | Motor Voltage | 16120 | 3EF8 | Uint16 | -1 | N2 | Normalized value 2 bytes
1613 | Frequency | 16130 | 3F02 | Uint16 | -1 | V2 | Bit sequence of 16 boolean variables
1614 | Motor Current | 16140 | 3F0C | Int32 | -2 | TimD | Time difference w/o date
1615 | Frequency [%] | 16150 | 3F16 | N2 | -2
1616 | Torque [Nm] | 16160 | 3F20 | Int32 | -1 | Conv. | Conv.
1617 | Speed [RPM] | 16170 | 3F2A | Int32 | 67 | index | factor
1618 | Motor Thermal | 16180 | 3F34 | Uint8 | 0 | 67 | 1/60
1622 | Torque [%] | 16220 | 3F5C | Int16 | 0 | 6 | 1000000
1630 | DC Link Voltage | 16300 | 3FAC | Uint16 | 0 | 5 | 100000
1632 | Brake Energy /s | 16320 | 3FC0 | Uint32 | 0 | 4 | 10000
1633 | Brake Energy /2 min | 16330 | 3FCA | Uint32 | 0 | 3 | 1000
1634 | Heatsink Temp. | 16340 | 3FD4 | Uint8 | 100 | 2 | 100
1635 | Inverter Thermal | 16350 | 3FDE | Uint8 | 0 | 1 | 10
1636 | Inv. Nom. Current | 16360 | 3FE8 | Uint32 | -2 | 0 | 1
1637 | Inv. Max. Current | 16370 | 3FF2 | Uint32 | -2 | -1 | 0.1
1638 | SL Controller State | 16380 | 3FFC | Uint8 | 0 | -2 | 0.01
1639 | Control Card Temp. | 16390 | 4006 | Uint8 | 100 | -3 | 0.001
1640 | Logging Buffer Full | 16400 | 4010 | Uint8 | -
1643 | Timed Actions Status | 16430 | 402E | Uint8 | -
1649 | Current Fault Source | 16490 | 406A | Uint8 | 0
1650 | External Reference | 16500 | 4074 | Int16 | -1
1652 | Feedback [Unit] | 16520 | 4088 | Int32 | -3
1653 | Digi Pot Reference | 16530 | 4092 | Int16 | -2
1654 | Feedback 1 [Unit] | 16540 | 409C | Int32 | -3
1655 | Feedback 2 [Unit] | 16550 | 40A6 | Int32 | -3
1656 | Feedback 3 [Unit] | 16560 | 40B0 | Int32 | -3
1658 | PID Output [%] | 16580 | 40C4 | Int16 | -1
1660 | Digital Input | 16600 | 40D8 | Uint16 | 0
1661 | Terminal 53 Switch Setting | 16610 | 40E2 | Uint8 | -
1662 | Analog Input 53 | 16620 | 40EC | Int32 | -3
1663 | Terminal 54 Switch Setting | 16630 | 40F6 | Uint8 | -
1664 | Analog Input 54 | 16640 | 4100 | Int32 | -3
1665 | Analog Output 42 [mA] | 16650 | 410A | Int16 | -3
1666 | Digital Output [bin] | 16660 | 4114 | Int16 | 0
1667 | Pulse Input #29 [Hz] | 16670 | 411E | Int32 | 0
1668 | Pulse Input #33 [Hz] | 16680 | 4128 | Int32 | 0
1669 | Pulse Output #27 [Hz] | 16690 | 4132 | Int32 | 0
1670 | Pulse Output #29 [Hz] | 16700 | 413C | Int32 | 0
1671 | Relay Output [bin] | 16710 | 4146 | Int16 | 0
1672 | Counter A | 16720 | 4150 | Int32 | 0
1673 | Counter B | 16730 | 415A | Int32 | 0
1680 | Fieldbus CTW 1 | 16800 | 41A0 | V2 | 0
1682 | Fieldbus REF 1 | 16820 | 41B4 | N2 | 0
1684 | Comm. Option STW | 16840 | 41C8 | V2 | 0
1685 | FC Port CTW 1 | 16850 | 41D2 | V2 | 0
1686 | FC Port REF 1 | 16860 | 41DC | N2 | 0
1690 | Alarm Word | 16900 | 4204 | Uint32 | 0
1691 | Alarm Word 2 | 16910 | 420E | Uint32 | 0
1692 | Warning Word | 16920 | 4218 | Uint32 | 0
1693 | Warning Word 2 | 16930 | 4222 | Uint32 | 0
1694 | Ext. Status Word | 16940 | 422C | Uint32 | 0
1695 | Ext. Status Word 2 | 16950 | 4236 | Uint32 | 0
1696 | Maintenance Word | 16960 | 4240 | Uint32 | 0

## FC102 Modbus Holding Registers
Danfoss FC102 Modbus RTU holding registers |  |  |  |  | 2008-11-05
Holding registers in yellow relate to drive array parameters. The array index of interest must be selected in holding register 7.
This list is for standard drive parameters.
Refer to Parameter Details for parameter size (data type) and scaling (conversion index).
| Modbus 4x Holding Register (decimal) | Par # | Name | Default Setting | Unit
| 1 | x | Reserved | 0
| 2 | x | Reserved | 0
| 3 | x | Reserved | 0
| 4 | x | Reserved | 0
| 5 | x | Reserved | 0
| 6 | x | Reserved | 0
| 7 | x | Last error code from an FC data object interface | 0
| 8 | x | Reserved | 0
| 9 | x | Parameter index | 0
| 10 | 1 | Language | English
| 20 | 2 | Motor Speed Unit | Hz
| 30 | 3 | Regional Settings | International
| 40 | 4 | Operating State at Power-up | Resume
| 50 | 5 | Local Mode Unit | As Motor Speed Unit
| 100 | 10 | Active Set-up | Set-up 1
| 110 | 11 | Programming Set-up | Active Set-up
| 120 | 12 | This Set-up Linked to | Not linked
| 130 | 13 | Readout: Linked Set-ups | {0}
|  | 13.1 | Readout: Linked Set-ups | {1}
|  | 13.2 | Readout: Linked Set-ups | {2}
|  | 13.3 | Readout: Linked Set-ups | {3}
|  | 13.4 | Readout: Linked Set-ups | {4}
| 140 | 14 | Readout: Prog. Set-ups / Channel | AAAAAAAAhex
| 200 | 20 | Display Line 1.1 Small | Reference [%]
| 210 | 21 | Display Line 1.2 Small | Motor Current
| 220 | 22 | Display Line 1.3 Small | Power [kW]
| 230 | 23 | Display Line 2 Large | Frequency
| 240 | 24 | Display Line 3 Large | kWh Counter
| 250 | 25 | My Personal Menu | 1
|  | 25.1 | My Personal Menu | 20
|  | 25.2 | My Personal Menu | 21
|  | 25.3 | My Personal Menu | 22
|  | 25.4 | My Personal Menu | 23
|  | 25.5 | My Personal Menu | 24
|  | 25.6 | My Personal Menu | 0
|  | 25.7 | My Personal Menu | 0
|  | 25.8 | My Personal Menu | 0
|  | 25.9 | My Personal Menu | 0
|  | 25.1 | My Personal Menu | 0
|  | 25.11 | My Personal Menu | 0
|  | 25.12 | My Personal Menu | 0
|  | 25.13 | My Personal Menu | 0
|  | 25.14 | My Personal Menu | 0
|  | 25.15 | My Personal Menu | 0
|  | 25.16 | My Personal Menu | 0
|  | 25.17 | My Personal Menu | 0
|  | 25.18 | My Personal Menu | 0
|  | 25.19 | My Personal Menu | 0
| 300 | 30 | Custom Readout Unit | %
| 310 | 31 | Custom Readout Min Value | 0 | %
| 320 | 32 | Custom Readout Max Value | 100 | %
| 370 | 37 | Display Text 1
| 380 | 38 | Display Text 2
| 390 | 39 | Display Text 3
| 400 | 40 | [Hand on] Key on LCP | Enabled
| 410 | 41 | [Off] Key on LCP | Enabled
| 420 | 42 | [Auto on] Key on LCP | Enabled
| 430 | 43 | [Reset] Key on LCP | Enabled
| 440 | 44 | [Off/Reset] Key on LCP | Enabled
| 450 | 45 | [Drive Bypass] Key on LCP | Enabled
| 500 | 50 | LCP Copy | No copy
| 510 | 51 | Set-up Copy | No copy
| 600 | 60 | Main Menu Password | 100
| 610 | 61 | Access to Main Menu w/o Password | Full access
| 650 | 65 | Personal Menu Password | 200
| 660 | 66 | Access to Personal Menu w/o Password | Full access
| 700 | 70 | Date and Time | 2007-01-01
| 710 | 71 | Date Format | DD-MM-YYYY
| 720 | 72 | Time Format | 24 h
| 740 | 74 | DST/Summertime | Off
| 760 | 76 | DST/Summertime Start | 2007-01-01 02:00
| 770 | 77 | DST/Summertime End | 2007-01-01 03:00
| 790 | 79 | Clock Fault | Disabled
| 810 | 81 | Working Days | Yes
|  | 81.1 | Working Days | Yes
|  | 81.2 | Working Days | Yes
|  | 81.3 | Working Days | Yes
|  | 81.4 | Working Days | Yes
|  | 81.5 | Working Days | No
|  | 81.6 | Working Days | No
| 820 | 82 | Additional Working Days | 2007-01-01
|  | 82.1 | Additional Working Days | 2007-01-01
|  | 82.2 | Additional Working Days | 2007-01-01
|  | 82.3 | Additional Working Days | 2007-01-01
|  | 82.4 | Additional Working Days | 2007-01-01
| 830 | 83 | Additional Non-Working Days | 2007-01-01
|  | 83.1 | Additional Non-Working Days | 2007-01-01
|  | 83.2 | Additional Non-Working Days | 2007-01-01
|  | 83.3 | Additional Non-Working Days | 2007-01-01
|  | 83.4 | Additional Non-Working Days | 2007-01-01
|  | 83.5 | Additional Non-Working Days | 2007-01-01
|  | 83.6 | Additional Non-Working Days | 2007-01-01
|  | 83.7 | Additional Non-Working Days | 2007-01-01
|  | 83.8 | Additional Non-Working Days | 2007-01-01
|  | 83.9 | Additional Non-Working Days | 2007-01-01
|  | 83.1 | Additional Non-Working Days | 2007-01-01
|  | 83.11 | Additional Non-Working Days | 2007-01-01
|  | 83.12 | Additional Non-Working Days | 2007-01-01
|  | 83.13 | Additional Non-Working Days | 2007-01-01
|  | 83.14 | Additional Non-Working Days | 2007-01-01
| 890 | 89 | Date and Time Readout
| 1000 | 100 | Configuration Mode | Open Loop
| 1030 | 103 | Torque Characteristics | Auto Energy Optim. VT
| 1200 | 120 | Motor Power [kW] | 22 | kW
| 1210 | 121 | Motor Power [HP] | 29.51 | hp
| 1220 | 122 | Motor Voltage | 400 | V
| 1230 | 123 | Motor Frequency | 50 | Hz
| 1240 | 124 | Motor Current | 42 | A
| 1250 | 125 | Motor Nominal Speed | 1460 | RPM
| 1280 | 128 | Motor Rotation Check | Off
| 1290 | 129 | Automatic Motor Adaptation (AMA) | Off
| 1300 | 130 | Stator Resistance (Rs) | 0.0896 | Ohm
| 1310 | 131 | Rotor Resistance (Rr) | 0.0775 | Ohm
| 1350 | 135 | Main Reactance (Xh) | 17.5954 | Ohm
| 1360 | 136 | Iron Loss Resistance (Rfe) | 378.945 | Ohm
| 1390 | 139 | Motor Poles | 4
| 1500 | 150 | Motor Magnetisation at Zero Speed | 100 | %
| 1510 | 151 | Min Speed Normal Magnetising [RPM] | 15 | RPM
| 1520 | 152 | Min Speed Normal Magnetising [Hz] | 0.5 | Hz
| 1600 | 160 | Low Speed Load Compensation | 100 | %
| 1610 | 161 | High Speed Load Compensation | 100 | %
| 1620 | 162 | Slip Compensation | 0 | %
| 1630 | 163 | Slip Compensation Time Constant | 0.1 | s
| 1640 | 164 | Resonance Dampening | 100 | %
| 1650 | 165 | Resonance Dampening Time Constant | 5 | ms
| 1710 | 171 | Start Delay | 0 | s
| 1730 | 173 | Flying Start | Disabled
| 1800 | 180 | Function at Stop | Coast
| 1810 | 181 | Min Speed for Function at Stop [RPM] | 3 | RPM
| 1820 | 182 | Min Speed for Function at Stop [Hz] | 0.1 | Hz
| 1860 | 186 | Trip Speed Low [RPM] | 0 | RPM
| 1870 | 187 | Trip Speed Low [Hz] | 0 | Hz
| 1900 | 190 | Motor Thermal Protection | ETR trip 1
| 1910 | 191 | Motor External Fan | No
| 1930 | 193 | Thermistor Source | None
| 2000 | 200 | DC Hold/Preheat Current | 50 | %
| 2010 | 201 | DC Brake Current | 50 | %
| 2020 | 202 | DC Braking Time | 10 | s
| 2030 | 203 | DC Brake Cut In Speed [RPM] | 0 | RPM
| 2040 | 204 | DC Brake Cut In Speed [Hz] | 0 | Hz
| 2100 | 210 | Brake Function | Off
| 2110 | 211 | Brake Resistor (ohm) | 20.4 | Ohm
| 2120 | 212 | Brake Power Limit (kW) | 29.6 | kW
| 2130 | 213 | Brake Power Monitoring | Off
| 2150 | 215 | Brake Check | Off
| 2160 | 216 | AC brake Max. Current | 100 | %
| 2170 | 217 | Over-voltage Control | Enabled
| 3020 | 302 | Minimum Reference | 0 | Hz
| 3030 | 303 | Maximum Reference | 50 | Hz
| 3040 | 304 | Reference Function | Sum
| 3100 | 310 | Preset Reference | 0 | %
|  | 310.1 | Preset Reference | 0 | %
|  | 310.2 | Preset Reference | 0 | %
|  | 310.3 | Preset Reference | 0 | %
|  | 310.4 | Preset Reference | 0 | %
|  | 310.5 | Preset Reference | 0 | %
|  | 310.6 | Preset Reference | 0 | %
|  | 310.7 | Preset Reference | 0 | %
| 3110 | 311 | Jog Speed [Hz] | 10 | Hz
| 3130 | 313 | Reference Site | Linked to Hand / Auto
| 3140 | 314 | Preset Relative Reference | 0 | %
| 3150 | 315 | Reference 1 Source | Analog input 53
| 3160 | 316 | Reference 2 Source | Digital pot.meter
| 3170 | 317 | Reference 3 Source | No function
| 3190 | 319 | Jog Speed [RPM] | 300 | RPM
| 3410 | 341 | Ramp 1 Ramp Up Time | 45 | s
| 3420 | 342 | Ramp 1 Ramp Down Time | 90 | s
| 3510 | 351 | Ramp 2 Ramp Up Time | 45 | s
| 3520 | 352 | Ramp 2 Ramp Down Time | 90 | s
| 3800 | 380 | Jog Ramp Time | 90 | s
| 3900 | 390 | Step Size | 0.1 | %
| 3910 | 391 | Ramp Time | 1 | s
| 3920 | 392 | Power Restore | Off
| 3930 | 393 | Maximum Limit | 100 | %
| 3940 | 394 | Minimum Limit | 0 | %
| 3950 | 395 | Ramp Delay | 0:00
| 4100 | 410 | Motor Speed Direction | Both directions
| 4110 | 411 | Motor Speed Low Limit [RPM] | 0 | RPM
| 4120 | 412 | Motor Speed Low Limit [Hz] | 0 | Hz
| 4130 | 413 | Motor Speed High Limit [RPM] | 1500 | RPM
| 4140 | 414 | Motor Speed High Limit [Hz] | 50 | Hz
| 4160 | 416 | Torque Limit Motor Mode | 115.2 | %
| 4170 | 417 | Torque Limit Generator Mode | 100 | %
| 4180 | 418 | Current Limit | 110 | %
| 4190 | 419 | Max Output Frequency | 100 | Hz
| 4500 | 450 | Warning Current Low | 0 | A
| 4510 | 451 | Warning Current High | 48.4 | A
| 4520 | 452 | Warning Speed Low | 0 | RPM
| 4530 | 453 | Warning Speed High | 1500 | RPM
| 4540 | 454 | Warning Reference Low | -999999.999
| 4550 | 455 | Warning Reference High | 999999.999
| 4560 | 456 | Warning Feedback Low | -999999.999 | %
| 4570 | 457 | Warning Feedback High | 999999.999 | %
| 4580 | 458 | Missing Motor Phase Function | Trip 1000 ms
| 4600 | 460 | Bypass Speed From [RPM] | 0 | RPM
|  | 460.1 | Bypass Speed From [RPM] | 0 | RPM
|  | 460.2 | Bypass Speed From [RPM] | 0 | RPM
|  | 460.3 | Bypass Speed From [RPM] | 0 | RPM
| 4610 | 461 | Bypass Speed From [Hz] | 0 | Hz
|  | 461.1 | Bypass Speed From [Hz] | 0 | Hz
|  | 461.2 | Bypass Speed From [Hz] | 0 | Hz
|  | 461.3 | Bypass Speed From [Hz] | 0 | Hz
| 4620 | 462 | Bypass Speed To [RPM] | 0 | RPM
|  | 462.1 | Bypass Speed To [RPM] | 0 | RPM
|  | 462.2 | Bypass Speed To [RPM] | 0 | RPM
|  | 462.3 | Bypass Speed To [RPM] | 0 | RPM
| 4630 | 463 | Bypass Speed To [Hz] | 0 | Hz
|  | 463.1 | Bypass Speed To [Hz] | 0 | Hz
|  | 463.2 | Bypass Speed To [Hz] | 0 | Hz
|  | 463.3 | Bypass Speed To [Hz] | 0 | Hz
| 4640 | 464 | Semi-Auto Bypass Set-up | Off
| 5000 | 500 | Digital I/O Mode | PNP - Active at 24V
| 5010 | 501 | Terminal 27 Mode | Input
| 5020 | 502 | Terminal 29 Mode | Input
| 5100 | 510 | Terminal 18 Digital Input | Start
| 5110 | 511 | Terminal 19 Digital Input | No operation
| 5120 | 512 | Terminal 27 Digital Input | Coast inverse
| 5130 | 513 | Terminal 29 Digital Input | Jog
| 5140 | 514 | Terminal 32 Digital Input | No operation
| 5150 | 515 | Terminal 33 Digital Input | No operation
| 5300 | 530 | Terminal 27 Digital Output | No operation
| 5310 | 531 | Terminal 29 Digital Output | No operation
| 5400 | 540 | Function Relay | Alarm
|  | 540.1 | Function Relay | Running
|  | 540.2 | Function Relay | No operation
|  | 540.3 | Function Relay | No operation
|  | 540.4 | Function Relay | No operation
|  | 540.5 | Function Relay | No operation
|  | 540.6 | Function Relay | No operation
|  | 540.7 | Function Relay | No operation
|  | 540.8 | Function Relay | No operation
| 5410 | 541 | On Delay, Relay | 0.01 | s
|  | 541.1 | On Delay, Relay | 0.01 | s
|  | 541.2 | On Delay, Relay | 0.01 | s
|  | 541.3 | On Delay, Relay | 0.01 | s
|  | 541.4 | On Delay, Relay | 0.01 | s
|  | 541.5 | On Delay, Relay | 0.01 | s
|  | 541.6 | On Delay, Relay | 0.01 | s
|  | 541.7 | On Delay, Relay | 0.01 | s
|  | 541.8 | On Delay, Relay | 0.01 | s
| 5420 | 542 | Off Delay, Relay | 0.01 | s
|  | 542.1 | Off Delay, Relay | 0.01 | s
|  | 542.2 | Off Delay, Relay | 0.01 | s
|  | 542.3 | Off Delay, Relay | 0.01 | s
|  | 542.4 | Off Delay, Relay | 0.01 | s
|  | 542.5 | Off Delay, Relay | 0.01 | s
|  | 542.6 | Off Delay, Relay | 0.01 | s
|  | 542.7 | Off Delay, Relay | 0.01 | s
|  | 542.8 | Off Delay, Relay | 0.01 | s
| 5500 | 550 | Term. 29 Low Frequency | 100 | Hz
| 5510 | 551 | Term. 29 High Frequency | 100 | Hz
| 5520 | 552 | Term. 29 Low Ref./Feedb. Value | 0
| 5530 | 553 | Term. 29 High Ref./Feedb. Value | 100
| 5540 | 554 | Pulse Filter Time Constant #29 | 100 | ms
| 5550 | 555 | Term. 33 Low Frequency | 100 | Hz
| 5560 | 556 | Term. 33 High Frequency | 100 | Hz
| 5570 | 557 | Term. 33 Low Ref./Feedb. Value | 0
| 5580 | 558 | Term. 33 High Ref./Feedb. Value | 100
| 5590 | 559 | Pulse Filter Time Constant #33 | 100 | ms
| 5600 | 560 | Terminal 27 Pulse Output Variable | No operation
| 5620 | 562 | Pulse Output Max Freq #27 | 5000 | Hz
| 5630 | 563 | Terminal 29 Pulse Output Variable | No operation
| 5650 | 565 | Pulse Output Max Freq #29 | 5000 | Hz
| 5900 | 590 | Digital & Relay Bus Control | 0hex
| 5930 | 593 | Pulse Out #27 Bus Control | 0 | %
| 5940 | 594 | Pulse Out #27 Timeout Preset | 0 | %
| 5950 | 595 | Pulse Out #29 Bus Control | 0 | %
| 5960 | 596 | Pulse Out #29 Timeout Preset | 0 | %
| 6000 | 600 | Live Zero Timeout Time | 10 | s
| 6010 | 601 | Live Zero Timeout Function | Off
| 6020 | 602 | Fire Mode Live Zero Timeout Function | Off
| 6100 | 610 | Terminal 53 Low Voltage | 0.07 | V
| 6110 | 611 | Terminal 53 High Voltage | 10 | V
| 6120 | 612 | Terminal 53 Low Current | 4 | mA
| 6130 | 613 | Terminal 53 High Current | 20 | mA
| 6140 | 614 | Terminal 53 Low Ref./Feedb. Value | 0
| 6150 | 615 | Terminal 53 High Ref./Feedb. Value | 50
| 6160 | 616 | Terminal 53 Filter Time Constant | 0.001 | s
| 6170 | 617 | Terminal 53 Live Zero | Enabled
| 6200 | 620 | Terminal 54 Low Voltage | 0.07 | V
| 6210 | 621 | Terminal 54 High Voltage | 10 | V
| 6220 | 622 | Terminal 54 Low Current | 4 | mA
| 6230 | 623 | Terminal 54 High Current | 20 | mA
| 6240 | 624 | Terminal 54 Low Ref./Feedb. Value | 0
| 6250 | 625 | Terminal 54 High Ref./Feedb. Value | 100
| 6260 | 626 | Terminal 54 Filter Time Constant | 0.001 | s
| 6270 | 627 | Terminal 54 Live Zero | Enabled
| 6500 | 650 | Terminal 42 Output | Speed 0-HighLim
| 6510 | 651 | Terminal 42 Output Min Scale | 0 | %
| 6520 | 652 | Terminal 42 Output Max Scale | 100 | %
| 6530 | 653 | Terminal 42 Output Bus Control | 0 | %
| 6540 | 654 | Terminal 42 Output Timeout Preset | 0 | %
| 8010 | 801 | Control Site | Digital and ctrl.word
| 8020 | 802 | Control Source | FC Port
| 8030 | 803 | Control Timeout Time | 60 | s
| 8040 | 804 | Control Timeout Function | Off
| 8050 | 805 | End-of-Timeout Function | Resume set-up
| 8060 | 806 | Reset Control Timeout | Do not reset
| 8070 | 807 | Diagnosis Trigger | Disable
| 8100 | 810 | Control Profile | FC profile
| 8130 | 813 | Configurable Status Word STW | Profile Default
|  | 813.1 | Configurable Status Word STW | Profile Default
|  | 813.1 | Configurable Status Word STW | Profile Default
|  | 813.11 | Configurable Status Word STW | Profile Default
|  | 813.12 | Configurable Status Word STW | Profile Default
|  | 813.13 | Configurable Status Word STW | Profile Default
|  | 813.14 | Configurable Status Word STW | Profile Default
|  | 813.15 | Configurable Status Word STW | Profile Default
|  | 813.2 | Configurable Status Word STW | Profile Default
|  | 813.3 | Configurable Status Word STW | Profile Default
|  | 813.4 | Configurable Status Word STW | Profile Default
|  | 813.5 | Configurable Status Word STW | Profile Default
|  | 813.6 | Configurable Status Word STW | Profile Default
|  | 813.7 | Configurable Status Word STW | Profile Default
|  | 813.8 | Configurable Status Word STW | Profile Default
|  | 813.9 | Configurable Status Word STW | Profile Default
| 8300 | 830 | Protocol | FC
| 8310 | 831 | Address | 1
| 8320 | 832 | Baud Rate | 9600 Baud
| 8330 | 833 | Parity / Stop Bits | Even Parity, 1 Stop Bit
| 8350 | 835 | Minimum Response Delay | 10 | ms
| 8360 | 836 | Maximum Response Delay | 10001 | ms
| 8370 | 837 | Maximum Inter-Char Delay | 35.01 | ms
| 8400 | 840 | Telegram Selection | Standard telegram 1
| 8500 | 850 | Coasting Select | Logic OR
| 8520 | 852 | DC Brake Select | Logic OR
| 8530 | 853 | Start Select | Logic OR
| 8540 | 854 | Reversing Select | Digital input
| 8550 | 855 | Set-up Select | Logic OR
| 8560 | 856 | Preset Reference Select | Logic OR
| 8800 | 880 | Bus Message Count | 0
| 8810 | 881 | Bus Error Count | 0
|  | 881.1 | Bus Error Count | 0
|  | 881.2 | Bus Error Count | 0
|  | 881.3 | Bus Error Count | 0
|  | 881.4 | Bus Error Count | 0
|  | 881.5 | Bus Error Count | 0
| 8820 | 882 | Slave Messages Rcvd | 0
| 8830 | 883 | Slave Error Count | 0
| 8840 | 884 | Slave Messages Sent | 0
| 8850 | 885 | Slave Timeout Errors | 0
| 13000 | 1300 | SL Controller Mode | Off
| 13010 | 1301 | Start Event | Start command
| 13020 | 1302 | Stop Event | Drive stopped
| 13100 | 1310 | Comparator Operand | DISABLED
|  | 1310.1 | Comparator Operand | DISABLED
|  | 1310.2 | Comparator Operand | DISABLED
|  | 1310.3 | Comparator Operand | DISABLED
|  | 1310.4 | Comparator Operand | DISABLED
|  | 1310.5 | Comparator Operand | DISABLED
| 13110 | 1311 | Comparator Operator | (equal)
|  | 1311.1 | Comparator Operator | (equal)
|  | 1311.2 | Comparator Operator | (equal)
|  | 1311.3 | Comparator Operator | (equal)
|  | 1311.4 | Comparator Operator | (equal)
|  | 1311.5 | Comparator Operator | (equal)
| 13120 | 1312 | Comparator Value | 0
|  | 1312.1 | Comparator Value | 0
|  | 1312.2 | Comparator Value | 0
|  | 1312.3 | Comparator Value | 0
|  | 1312.4 | Comparator Value | 0
|  | 1312.5 | Comparator Value | 0
| 13200 | 1320 | SL Controller Timer | 0:00
|  | 1320.1 | SL Controller Timer | 0:00
|  | 1320.2 | SL Controller Timer | 0:00
|  | 1320.3 | SL Controller Timer | 0:00
|  | 1320.4 | SL Controller Timer | 0:00
|  | 1320.5 | SL Controller Timer | 0:00
|  | 1320.6 | SL Controller Timer | 0:00
|  | 1320.7 | SL Controller Timer | 0:00
| 13400 | 1340 | Logic Rule Boolean 1 | FALSE
|  | 1340.1 | Logic Rule Boolean 1 | FALSE
|  | 1340.2 | Logic Rule Boolean 1 | FALSE
|  | 1340.3 | Logic Rule Boolean 1 | FALSE
|  | 1340.4 | Logic Rule Boolean 1 | FALSE
|  | 1340.5 | Logic Rule Boolean 1 | FALSE
| 13410 | 1341 | Logic Rule Operator 1 | DISABLED
|  | 1341.1 | Logic Rule Operator 1 | DISABLED
|  | 1341.2 | Logic Rule Operator 1 | DISABLED
|  | 1341.3 | Logic Rule Operator 1 | DISABLED
|  | 1341.4 | Logic Rule Operator 1 | DISABLED
|  | 1341.5 | Logic Rule Operator 1 | DISABLED
| 13420 | 1342 | Logic Rule Boolean 2 | FALSE
|  | 1342.1 | Logic Rule Boolean 2 | FALSE
|  | 1342.2 | Logic Rule Boolean 2 | FALSE
|  | 1342.3 | Logic Rule Boolean 2 | FALSE
|  | 1342.4 | Logic Rule Boolean 2 | FALSE
|  | 1342.5 | Logic Rule Boolean 2 | FALSE
| 13430 | 1343 | Logic Rule Operator 2 | DISABLED
|  | 1343.1 | Logic Rule Operator 2 | DISABLED
|  | 1343.2 | Logic Rule Operator 2 | DISABLED
|  | 1343.3 | Logic Rule Operator 2 | DISABLED
|  | 1343.4 | Logic Rule Operator 2 | DISABLED
|  | 1343.5 | Logic Rule Operator 2 | DISABLED
| 13440 | 1344 | Logic Rule Boolean 3 | FALSE
|  | 1344.1 | Logic Rule Boolean 3 | FALSE
|  | 1344.2 | Logic Rule Boolean 3 | FALSE
|  | 1344.3 | Logic Rule Boolean 3 | FALSE
|  | 1344.4 | Logic Rule Boolean 3 | FALSE
|  | 1344.5 | Logic Rule Boolean 3 | FALSE
| 13510 | 1351 | SL Controller Event | FALSE
|  | 1351.1 | SL Controller Event | FALSE
|  | 1351.1 | SL Controller Event | FALSE
|  | 1351.11 | SL Controller Event | FALSE
|  | 1351.12 | SL Controller Event | FALSE
|  | 1351.13 | SL Controller Event | FALSE
|  | 1351.14 | SL Controller Event | FALSE
|  | 1351.15 | SL Controller Event | FALSE
|  | 1351.16 | SL Controller Event | FALSE
|  | 1351.17 | SL Controller Event | FALSE
|  | 1351.18 | SL Controller Event | FALSE
|  | 1351.19 | SL Controller Event | FALSE
|  | 1351.2 | SL Controller Event | FALSE
|  | 1351.3 | SL Controller Event | FALSE
|  | 1351.4 | SL Controller Event | FALSE
|  | 1351.5 | SL Controller Event | FALSE
|  | 1351.6 | SL Controller Event | FALSE
|  | 1351.7 | SL Controller Event | FALSE
|  | 1351.8 | SL Controller Event | FALSE
|  | 1351.9 | SL Controller Event | FALSE
| 13520 | 1352 | SL Controller Action | Disabled
|  | 1352.1 | SL Controller Action | Disabled
|  | 1352.1 | SL Controller Action | Disabled
|  | 1352.11 | SL Controller Action | Disabled
|  | 1352.12 | SL Controller Action | Disabled
|  | 1352.13 | SL Controller Action | Disabled
|  | 1352.14 | SL Controller Action | Disabled
|  | 1352.15 | SL Controller Action | Disabled
|  | 1352.16 | SL Controller Action | Disabled
|  | 1352.17 | SL Controller Action | Disabled
|  | 1352.18 | SL Controller Action | Disabled
|  | 1352.19 | SL Controller Action | Disabled
|  | 1352.2 | SL Controller Action | Disabled
|  | 1352.3 | SL Controller Action | Disabled
|  | 1352.4 | SL Controller Action | Disabled
|  | 1352.5 | SL Controller Action | Disabled
|  | 1352.6 | SL Controller Action | Disabled
|  | 1352.7 | SL Controller Action | Disabled
|  | 1352.8 | SL Controller Action | Disabled
|  | 1352.9 | SL Controller Action | Disabled
| 14000 | 1400 | Switching Pattern | 60 AVM
| 14010 | 1401 | Switching Frequency | 4.0 kHz
| 14030 | 1403 | Overmodulation | On
| 14040 | 1404 | PWM Random | Off
| 14100 | 1410 | Mains Failure | No function
| 14110 | 1411 | Mains Voltage at Mains Fault | 342 | V
| 14120 | 1412 | Function at Mains Imbalance | Trip
| 14200 | 1420 | Reset Mode | Manual reset
| 14210 | 1421 | Automatic Restart Time | 10 | s
| 14220 | 1422 | Operation Mode | Normal operation
| 14250 | 1425 | Trip Delay at Torque Limit | 60 | s
| 14260 | 1426 | Trip Delay at Inverter Fault | 4 | s
| 14300 | 1430 | Current Lim Ctrl, Proportional Gain | 100 | %
| 14310 | 1431 | Current Lim Ctrl, Integration Time | 0.02 | s
| 14320 | 1432 | Current Lim Ctrl, Filter Time | 26 | ms
| 14400 | 1440 | VT Level | 66 | %
| 14410 | 1441 | AEO Minimum Magnetisation | 45 | %
| 14420 | 1442 | Minimum AEO Frequency | 10 | Hz
| 14430 | 1443 | Motor Cosphi | 0.81
| 14500 | 1450 | RFI Filter | On
| 14520 | 1452 | Fan Control | Auto
| 14530 | 1453 | Fan Monitor | Warning
| 14590 | 1459 | Actual Number of Inverter Units | 1
| 14600 | 1460 | Function at Over Temperature | Trip
| 14610 | 1461 | Function at Inverter Overload | Trip
| 14620 | 1462 | Inv. Overload Derate Current | 95 | %
| 15000 | 1500 | Operating Hours | 0 | h
| 15010 | 1501 | Running Hours | 0 | h
| 15020 | 1502 | kWh Counter | 0 | kWh
| 15030 | 1503 | Power Up's | 0
| 15040 | 1504 | Over Temp's | 0
| 15050 | 1505 | Over Volt's | 0
| 15060 | 1506 | Reset kWh Counter | Do not reset
| 15070 | 1507 | Reset Running Hours Counter | Do not reset
| 15080 | 1508 | Number of Starts | 0
| 15100 | 1510 | Logging Source | None
|  | 1510.1 | Logging Source | None
|  | 1510.2 | Logging Source | None
|  | 1510.3 | Logging Source | None
| 15110 | 1511 | Logging Interval | 0:00
|  | 1511.1 | Logging Interval | 0:00
|  | 1511.2 | Logging Interval | 0:00
|  | 1511.3 | Logging Interval | 0:00
| 15120 | 1512 | Trigger Event | FALSE
| 15130 | 1513 | Logging Mode | Log always
| 15140 | 1514 | Samples Before Trigger | 50
| 15200 | 1520 | Historic Log: Event | 0
|  | 1520.1 | Historic Log: Event | 0
|  | 1520.2 | Historic Log: Event | 0
|  | 1520.3 | Historic Log: Event | 0
|  | 1520.4 | Historic Log: Event | 0
|  | 1520.5 | Historic Log: Event | 0
|  | 1520.6 | Historic Log: Event | 0
|  | 1520.7 | Historic Log: Event | 0
|  | 1520.8 | Historic Log: Event | 0
|  | 1520.9 | Historic Log: Event | 0
|  | 1520.1 | Historic Log: Event | 0
|  | 1520.11 | Historic Log: Event | 0
|  | 1520.12 | Historic Log: Event | 0
|  | 1520.13 | Historic Log: Event | 0
|  | 1520.14 | Historic Log: Event | 0
|  | 1520.15 | Historic Log: Event | 0
|  | 1520.16 | Historic Log: Event | 0
|  | 1520.17 | Historic Log: Event | 0
|  | 1520.18 | Historic Log: Event | 0
|  | 1520.19 | Historic Log: Event | 0
|  | 1520.2 | Historic Log: Event | 0
|  | 1520.21 | Historic Log: Event | 0
|  | 1520.22 | Historic Log: Event | 0
|  | 1520.23 | Historic Log: Event | 0
|  | 1520.24 | Historic Log: Event | 0
|  | 1520.25 | Historic Log: Event | 0
|  | 1520.26 | Historic Log: Event | 0
|  | 1520.27 | Historic Log: Event | 0
|  | 1520.28 | Historic Log: Event | 0
|  | 1520.29 | Historic Log: Event | 0
|  | 1520.3 | Historic Log: Event | 0
|  | 1520.31 | Historic Log: Event | 0
|  | 1520.32 | Historic Log: Event | 0
|  | 1520.33 | Historic Log: Event | 0
|  | 1520.34 | Historic Log: Event | 0
|  | 1520.35 | Historic Log: Event | 0
|  | 1520.36 | Historic Log: Event | 0
|  | 1520.37 | Historic Log: Event | 0
|  | 1520.38 | Historic Log: Event | 0
|  | 1520.39 | Historic Log: Event | 0
|  | 1520.4 | Historic Log: Event | 0
|  | 1520.41 | Historic Log: Event | 0
|  | 1520.42 | Historic Log: Event | 0
|  | 1520.43 | Historic Log: Event | 0
|  | 1520.44 | Historic Log: Event | 0
|  | 1520.45 | Historic Log: Event | 0
|  | 1520.46 | Historic Log: Event | 0
|  | 1520.47 | Historic Log: Event | 0
|  | 1520.48 | Historic Log: Event | 0
|  | 1520.49 | Historic Log: Event | 0
| 15210 | 1521 | Historic Log: Value | 0
|  | 1521.1 | Historic Log: Value | 0
|  | 1521.2 | Historic Log: Value | 0
|  | 1521.3 | Historic Log: Value | 0
|  | 1521.4 | Historic Log: Value | 0
|  | 1521.5 | Historic Log: Value | 0
|  | 1521.6 | Historic Log: Value | 0
|  | 1521.7 | Historic Log: Value | 0
|  | 1521.8 | Historic Log: Value | 0
|  | 1521.9 | Historic Log: Value | 0
|  | 1521.1 | Historic Log: Value | 0
|  | 1521.11 | Historic Log: Value | 0
|  | 1521.12 | Historic Log: Value | 0
|  | 1521.13 | Historic Log: Value | 0
|  | 1521.14 | Historic Log: Value | 0
|  | 1521.15 | Historic Log: Value | 0
|  | 1521.16 | Historic Log: Value | 0
|  | 1521.17 | Historic Log: Value | 0
|  | 1521.18 | Historic Log: Value | 0
|  | 1521.19 | Historic Log: Value | 0
|  | 1521.2 | Historic Log: Value | 0
|  | 1521.21 | Historic Log: Value | 0
|  | 1521.22 | Historic Log: Value | 0
|  | 1521.23 | Historic Log: Value | 0
|  | 1521.24 | Historic Log: Value | 0
|  | 1521.25 | Historic Log: Value | 0
|  | 1521.26 | Historic Log: Value | 0
|  | 1521.27 | Historic Log: Value | 0
|  | 1521.28 | Historic Log: Value | 0
|  | 1521.29 | Historic Log: Value | 0
|  | 1521.3 | Historic Log: Value | 0
|  | 1521.31 | Historic Log: Value | 0
|  | 1521.32 | Historic Log: Value | 0
|  | 1521.33 | Historic Log: Value | 0
|  | 1521.34 | Historic Log: Value | 0
|  | 1521.35 | Historic Log: Value | 0
|  | 1521.36 | Historic Log: Value | 0
|  | 1521.37 | Historic Log: Value | 0
|  | 1521.38 | Historic Log: Value | 0
|  | 1521.39 | Historic Log: Value | 0
|  | 1521.4 | Historic Log: Value | 0
|  | 1521.41 | Historic Log: Value | 0
|  | 1521.42 | Historic Log: Value | 0
|  | 1521.43 | Historic Log: Value | 0
|  | 1521.44 | Historic Log: Value | 0
|  | 1521.45 | Historic Log: Value | 0
|  | 1521.46 | Historic Log: Value | 0
|  | 1521.47 | Historic Log: Value | 0
|  | 1521.48 | Historic Log: Value | 0
|  | 1521.49 | Historic Log: Value | 0
| 15220 | 1522 | Historic Log: Time | 0 | ms
|  | 1522.1 | Historic Log: Time | 0 | ms
|  | 1522.2 | Historic Log: Time | 0 | ms
|  | 1522.3 | Historic Log: Time | 0 | ms
|  | 1522.4 | Historic Log: Time | 0 | ms
|  | 1522.5 | Historic Log: Time | 0 | ms
|  | 1522.6 | Historic Log: Time | 0 | ms
|  | 1522.7 | Historic Log: Time | 0 | ms
|  | 1522.8 | Historic Log: Time | 0 | ms
|  | 1522.9 | Historic Log: Time | 0 | ms
|  | 1522.1 | Historic Log: Time | 0 | ms
|  | 1522.11 | Historic Log: Time | 0 | ms
|  | 1522.12 | Historic Log: Time | 0 | ms
|  | 1522.13 | Historic Log: Time | 0 | ms
|  | 1522.14 | Historic Log: Time | 0 | ms
|  | 1522.15 | Historic Log: Time | 0 | ms
|  | 1522.16 | Historic Log: Time | 0 | ms
|  | 1522.17 | Historic Log: Time | 0 | ms
|  | 1522.18 | Historic Log: Time | 0 | ms
|  | 1522.19 | Historic Log: Time | 0 | ms
|  | 1522.2 | Historic Log: Time | 0 | ms
|  | 1522.21 | Historic Log: Time | 0 | ms
|  | 1522.22 | Historic Log: Time | 0 | ms
|  | 1522.23 | Historic Log: Time | 0 | ms
|  | 1522.24 | Historic Log: Time | 0 | ms
|  | 1522.25 | Historic Log: Time | 0 | ms
|  | 1522.26 | Historic Log: Time | 0 | ms
|  | 1522.27 | Historic Log: Time | 0 | ms
|  | 1522.28 | Historic Log: Time | 0 | ms
|  | 1522.29 | Historic Log: Time | 0 | ms
|  | 1522.3 | Historic Log: Time | 0 | ms
|  | 1522.31 | Historic Log: Time | 0 | ms
|  | 1522.32 | Historic Log: Time | 0 | ms
|  | 1522.33 | Historic Log: Time | 0 | ms
|  | 1522.34 | Historic Log: Time | 0 | ms
|  | 1522.35 | Historic Log: Time | 0 | ms
|  | 1522.36 | Historic Log: Time | 0 | ms
|  | 1522.37 | Historic Log: Time | 0 | ms
|  | 1522.38 | Historic Log: Time | 0 | ms
|  | 1522.39 | Historic Log: Time | 0 | ms
|  | 1522.4 | Historic Log: Time | 0 | ms
|  | 1522.41 | Historic Log: Time | 0 | ms
|  | 1522.42 | Historic Log: Time | 0 | ms
|  | 1522.43 | Historic Log: Time | 0 | ms
|  | 1522.44 | Historic Log: Time | 0 | ms
|  | 1522.45 | Historic Log: Time | 0 | ms
|  | 1522.46 | Historic Log: Time | 0 | ms
|  | 1522.47 | Historic Log: Time | 0 | ms
|  | 1522.48 | Historic Log: Time | 0 | ms
|  | 1522.49 | Historic Log: Time | 0 | ms
| 15230 | 1523 | Historic Log: Date and Time | 1984-01-01
|  | 1523.1 | Historic Log: Date and Time | 1984-01-01
|  | 1523.2 | Historic Log: Date and Time | 1984-01-01
|  | 1523.3 | Historic Log: Date and Time | 1984-01-01
|  | 1523.4 | Historic Log: Date and Time | 1984-01-01
|  | 1523.5 | Historic Log: Date and Time | 1984-01-01
|  | 1523.6 | Historic Log: Date and Time | 1984-01-01
|  | 1523.7 | Historic Log: Date and Time | 1984-01-01
|  | 1523.8 | Historic Log: Date and Time | 1984-01-01
|  | 1523.9 | Historic Log: Date and Time | 1984-01-01
|  | 1523.1 | Historic Log: Date and Time | 1984-01-01
|  | 1523.11 | Historic Log: Date and Time | 1984-01-01
|  | 1523.12 | Historic Log: Date and Time | 1984-01-01
|  | 1523.13 | Historic Log: Date and Time | 1984-01-01
|  | 1523.14 | Historic Log: Date and Time | 1984-01-01
|  | 1523.15 | Historic Log: Date and Time | 1984-01-01
|  | 1523.16 | Historic Log: Date and Time | 1984-01-01
|  | 1523.17 | Historic Log: Date and Time | 1984-01-01
|  | 1523.18 | Historic Log: Date and Time | 1984-01-01
|  | 1523.19 | Historic Log: Date and Time | 1984-01-01
|  | 1523.2 | Historic Log: Date and Time | 1984-01-01
|  | 1523.21 | Historic Log: Date and Time | 1984-01-01
|  | 1523.22 | Historic Log: Date and Time | 1984-01-01
|  | 1523.23 | Historic Log: Date and Time | 1984-01-01
|  | 1523.24 | Historic Log: Date and Time | 1984-01-01
|  | 1523.25 | Historic Log: Date and Time | 1984-01-01
|  | 1523.26 | Historic Log: Date and Time | 1984-01-01
|  | 1523.27 | Historic Log: Date and Time | 1984-01-01
|  | 1523.28 | Historic Log: Date and Time | 1984-01-01
|  | 1523.29 | Historic Log: Date and Time | 1984-01-01
|  | 1523.3 | Historic Log: Date and Time | 1984-01-01
|  | 1523.31 | Historic Log: Date and Time | 1984-01-01
|  | 1523.32 | Historic Log: Date and Time | 1984-01-01
|  | 1523.33 | Historic Log: Date and Time | 1984-01-01
|  | 1523.34 | Historic Log: Date and Time | 1984-01-01
|  | 1523.35 | Historic Log: Date and Time | 1984-01-01
|  | 1523.36 | Historic Log: Date and Time | 1984-01-01
|  | 1523.37 | Historic Log: Date and Time | 1984-01-01
|  | 1523.38 | Historic Log: Date and Time | 1984-01-01
|  | 1523.39 | Historic Log: Date and Time | 1984-01-01
|  | 1523.4 | Historic Log: Date and Time | 1984-01-01
|  | 1523.41 | Historic Log: Date and Time | 1984-01-01
|  | 1523.42 | Historic Log: Date and Time | 1984-01-01
|  | 1523.43 | Historic Log: Date and Time | 1984-01-01
|  | 1523.44 | Historic Log: Date and Time | 1984-01-01
|  | 1523.45 | Historic Log: Date and Time | 1984-01-01
|  | 1523.46 | Historic Log: Date and Time | 1984-01-01
|  | 1523.47 | Historic Log: Date and Time | 1984-01-01
|  | 1523.48 | Historic Log: Date and Time | 1984-01-01
|  | 1523.49 | Historic Log: Date and Time | 1984-01-01
| 15300 | 1530 | Alarm Log: Error Code | 1
|  | 1530.1 | Alarm Log: Error Code | 2
|  | 1530.2 | Alarm Log: Error Code | 3
|  | 1530.3 | Alarm Log: Error Code | 4
|  | 1530.4 | Alarm Log: Error Code | 5
|  | 1530.5 | Alarm Log: Error Code | 6
|  | 1530.6 | Alarm Log: Error Code | 7
|  | 1530.7 | Alarm Log: Error Code | 8
|  | 1530.8 | Alarm Log: Error Code | 9
|  | 1530.9 | Alarm Log: Error Code | 10
| 15310 | 1531 | Alarm Log: Value | 4
|  | 1531.1 | Alarm Log: Value | 11
|  | 1531.2 | Alarm Log: Value | 18
|  | 1531.3 | Alarm Log: Value | 25
|  | 1531.4 | Alarm Log: Value | 32
|  | 1531.5 | Alarm Log: Value | 39
|  | 1531.6 | Alarm Log: Value | 46
|  | 1531.7 | Alarm Log: Value | 53
|  | 1531.8 | Alarm Log: Value | 60
|  | 1531.9 | Alarm Log: Value | 67
| 15320 | 1532 | Alarm Log: Time | 7 | s
|  | 1532.1 | Alarm Log: Time | 11 | s
|  | 1532.2 | Alarm Log: Time | 15 | s
|  | 1532.3 | Alarm Log: Time | 19 | s
|  | 1532.4 | Alarm Log: Time | 23 | s
|  | 1532.5 | Alarm Log: Time | 27 | s
|  | 1532.6 | Alarm Log: Time | 31 | s
|  | 1532.7 | Alarm Log: Time | 35 | s
|  | 1532.8 | Alarm Log: Time | 39 | s
|  | 1532.9 | Alarm Log: Time | 43 | s
| 15330 | 1533 | Alarm Log: Date and Time | 1984-01-01
|  | 1533.1 | Alarm Log: Date and Time | 1984-01-01
|  | 1533.2 | Alarm Log: Date and Time | 1984-01-01
|  | 1533.3 | Alarm Log: Date and Time | 1984-01-01
|  | 1533.4 | Alarm Log: Date and Time | 1984-01-01
|  | 1533.5 | Alarm Log: Date and Time | 1984-01-01
|  | 1533.6 | Alarm Log: Date and Time | 1984-01-01
|  | 1533.7 | Alarm Log: Date and Time | 1984-01-01
|  | 1533.8 | Alarm Log: Date and Time | 1984-01-01
|  | 1533.9 | Alarm Log: Date and Time | 1984-01-01
| 15400 | 1540 | FC Type
| 15410 | 1541 | Power Section
| 15420 | 1542 | Voltage
| 15430 | 1543 | Software Version
| 15440 | 1544 | Ordered Typecode String
| 15450 | 1545 | Actual Typecode String
| 15460 | 1546 | Frequency Converter Ordering No
| 15470 | 1547 | Power Card Ordering No
| 15480 | 1548 | LCP Id No
| 15490 | 1549 | SW ID Control Card
| 15500 | 1550 | SW ID Power Card
| 15510 | 1551 | Frequency Converter Serial Number
| 15530 | 1553 | Power Card Serial Number
| 15600 | 1560 | Option Mounted
|  | 1560.1 | Option Mounted
|  | 1560.2 | Option Mounted
|  | 1560.3 | Option Mounted
|  | 1560.4 | Option Mounted
|  | 1560.5 | Option Mounted
|  | 1560.6 | Option Mounted
|  | 1560.7 | Option Mounted
| 15610 | 1561 | Option SW Version
|  | 1561.1 | Option SW Version
|  | 1561.2 | Option SW Version
|  | 1561.3 | Option SW Version
|  | 1561.4 | Option SW Version
|  | 1561.5 | Option SW Version
|  | 1561.6 | Option SW Version
|  | 1561.7 | Option SW Version
| 15620 | 1562 | Option Ordering No
|  | 1562.1 | Option Ordering No
|  | 1562.2 | Option Ordering No
|  | 1562.3 | Option Ordering No
|  | 1562.4 | Option Ordering No
|  | 1562.5 | Option Ordering No
|  | 1562.6 | Option Ordering No
|  | 1562.7 | Option Ordering No
| 15630 | 1563 | Option Serial No
|  | 1563.1 | Option Serial No
|  | 1563.2 | Option Serial No
|  | 1563.3 | Option Serial No
|  | 1563.4 | Option Serial No
|  | 1563.5 | Option Serial No
|  | 1563.6 | Option Serial No
|  | 1563.7 | Option Serial No
| 15990 | 1599 | Parameter Metadata | 12
|  | 1599.1 | Parameter Metadata | 1541
|  | 1599.1 | Parameter Metadata | 51
|  | 1599.11 | Parameter Metadata | 11
|  | 1599.12 | Parameter Metadata | 1542
|  | 1599.13 | Parameter Metadata | 1540
|  | 1599.14 | Parameter Metadata | 10
|  | 1599.15 | Parameter Metadata | 13
|  | 1599.16 | Parameter Metadata | 3
|  | 1599.17 | Parameter Metadata | 1553
|  | 1599.18 | Parameter Metadata | 1551
|  | 1599.19 | Parameter Metadata | 831
|  | 1599.2 | Parameter Metadata | 1544
|  | 1599.2 | Parameter Metadata | 832
|  | 1599.21 | Parameter Metadata | 918
|  | 1599.22 | Parameter Metadata | 1549
|  | 1599.23 | Parameter Metadata | 1560
|  | 1599.24 | Parameter Metadata | 1561
|  | 1599.25 | Parameter Metadata | 2
|  | 1599.26 | Parameter Metadata | 1576
|  | 1599.27 | Parameter Metadata | 1577
|  | 1599.28 | Parameter Metadata | 0
|  | 1599.29 | Parameter Metadata | 0
|  | 1599.3 | Parameter Metadata | 1570
|  | 1599.4 | Parameter Metadata | 1571
|  | 1599.5 | Parameter Metadata | 1572
|  | 1599.6 | Parameter Metadata | 1573
|  | 1599.7 | Parameter Metadata | 1574
|  | 1599.8 | Parameter Metadata | 1575
|  | 1599.9 | Parameter Metadata | 1543
| 16000 | 1600 | Control Word | 0hex
| 16010 | 1601 | Reference [Unit] | 0 | Hz
| 16020 | 1602 | Reference [%] | 0 | %
| 16030 | 1603 | Status Word | 0hex
| 16050 | 1605 | Main Actual Value [%] | 0 | %
| 16090 | 1609 | Custom Readout | 0.03 | %
| 16100 | 1610 | Power [kW] | 0 | kW
| 16110 | 1611 | Power [hp] | 0 | hp
| 16120 | 1612 | Motor Voltage | 0 | V
| 16130 | 1613 | Frequency | 0 | Hz
| 16140 | 1614 | Motor Current | 0 | A
| 16150 | 1615 | Frequency [%] | 0 | %
| 16160 | 1616 | Torque [Nm] | 0 | Nm
| 16170 | 1617 | Speed [RPM] | 0 | RPM
| 16180 | 1618 | Motor Thermal | 0 | %
| 16220 | 1622 | Torque [%] | 0 | %
| 16300 | 1630 | DC Link Voltage | 0 | V
| 16320 | 1632 | Brake Energy /s | 0 | kW
| 16330 | 1633 | Brake Energy /2 min | 0 | kW
| 16340 | 1634 | Heatsink Temp. | 0 | C
| 16350 | 1635 | Inverter Thermal | 0 | %
| 16360 | 1636 | Inv. Nom. Current | 44 | A
| 16370 | 1637 | Inv. Max. Current | 48.4 | A
| 16380 | 1638 | SL Controller State | 0
| 16390 | 1639 | Control Card Temp. | 0 | C
| 16400 | 1640 | Logging Buffer Full | No
| 16500 | 1650 | External Reference | 0
| 16520 | 1652 | Feedback [Unit] | 0 | %
| 16530 | 1653 | Digi Pot Reference | 0
| 16540 | 1654 | Feedback 1 [Unit] | 0 | %
| 16550 | 1655 | Feedback 2 [Unit] | 0 | %
| 16560 | 1656 | Feedback 3 [Unit] | 0 | %
| 16580 | 1658 | PID Output [%] | 0 | %
| 16600 | 1660 | Digital Input | 0000000000bin
| 16610 | 1661 | Terminal 53 Switch Setting | Voltage
| 16620 | 1662 | Analog Input 53 | 0
| 16630 | 1663 | Terminal 54 Switch Setting | Voltage
| 16640 | 1664 | Analog Input 54 | 0
| 16650 | 1665 | Analog Output 42 [mA] | 0
| 16660 | 1666 | Digital Output [bin] | 0000bin
| 16670 | 1667 | Pulse Input #29 [Hz] | 0
| 16680 | 1668 | Pulse Input #33 [Hz] | 0
| 16690 | 1669 | Pulse Output #27 [Hz] | 0
| 16700 | 1670 | Pulse Output #29 [Hz] | 0
| 16710 | 1671 | Relay Output [bin] | 000000000bin
| 16720 | 1672 | Counter A | 0
| 16730 | 1673 | Counter B | 0
| 16800 | 1680 | Fieldbus CTW 1 | 0hex
| 16820 | 1682 | Fieldbus REF 1 | FFFFF200hex
| 16840 | 1684 | Comm. Option STW | 0hex
| 16850 | 1685 | FC Port CTW 1 | F200hex
| 16860 | 1686 | FC Port REF 1 | FFFFF201hex
| 16900 | 1690 | Alarm Word | 0hex
| 16910 | 1691 | Alarm Word 2 | 0hex
| 16920 | 1692 | Warning Word | 0hex
| 16930 | 1693 | Warning Word 2 | 0hex
| 16940 | 1694 | Ext. Status Word | 0hex
| 16950 | 1695 | Ext. Status Word 2 | 0hex
| 16960 | 1696 | Maintenance Word | 0hex
| 18000 | 1800 | Maintenance Log: Item | 0
|  | 1800.1 | Maintenance Log: Item | 0
|  | 1800.2 | Maintenance Log: Item | 0
|  | 1800.3 | Maintenance Log: Item | 0
|  | 1800.4 | Maintenance Log: Item | 0
|  | 1800.5 | Maintenance Log: Item | 0
|  | 1800.6 | Maintenance Log: Item | 0
|  | 1800.7 | Maintenance Log: Item | 0
|  | 1800.8 | Maintenance Log: Item | 0
|  | 1800.9 | Maintenance Log: Item | 0
| 18010 | 1801 | Maintenance Log: Action | 0
|  | 1801.1 | Maintenance Log: Action | 0
|  | 1801.2 | Maintenance Log: Action | 0
|  | 1801.3 | Maintenance Log: Action | 0
|  | 1801.4 | Maintenance Log: Action | 0
|  | 1801.5 | Maintenance Log: Action | 0
|  | 1801.6 | Maintenance Log: Action | 0
|  | 1801.7 | Maintenance Log: Action | 0
|  | 1801.8 | Maintenance Log: Action | 0
|  | 1801.9 | Maintenance Log: Action | 0
| 18020 | 1802 | Maintenance Log: Time | 0 | s
|  | 1802.1 | Maintenance Log: Time | 0 | s
|  | 1802.2 | Maintenance Log: Time | 0 | s
|  | 1802.3 | Maintenance Log: Time | 0 | s
|  | 1802.4 | Maintenance Log: Time | 0 | s
|  | 1802.5 | Maintenance Log: Time | 0 | s
|  | 1802.6 | Maintenance Log: Time | 0 | s
|  | 1802.7 | Maintenance Log: Time | 0 | s
|  | 1802.8 | Maintenance Log: Time | 0 | s
|  | 1802.9 | Maintenance Log: Time | 0 | s
| 18030 | 1803 | Maintenance Log: Date and Time | 2005-01-01
|  | 1803.1 | Maintenance Log: Date and Time | 2005-01-01
|  | 1803.2 | Maintenance Log: Date and Time | 2005-01-01
|  | 1803.3 | Maintenance Log: Date and Time | 2005-01-01
|  | 1803.4 | Maintenance Log: Date and Time | 2005-01-01
|  | 1803.5 | Maintenance Log: Date and Time | 2005-01-01
|  | 1803.6 | Maintenance Log: Date and Time | 2005-01-01
|  | 1803.7 | Maintenance Log: Date and Time | 2005-01-01
|  | 1803.8 | Maintenance Log: Date and Time | 2005-01-01
|  | 1803.9 | Maintenance Log: Date and Time | 2005-01-01
| 18100 | 1810 | Fire Mode Log: Event | 0
|  | 1810.1 | Fire Mode Log: Event | 0
|  | 1810.2 | Fire Mode Log: Event | 0
|  | 1810.3 | Fire Mode Log: Event | 0
|  | 1810.4 | Fire Mode Log: Event | 0
|  | 1810.5 | Fire Mode Log: Event | 0
|  | 1810.6 | Fire Mode Log: Event | 0
|  | 1810.7 | Fire Mode Log: Event | 0
|  | 1810.8 | Fire Mode Log: Event | 0
|  | 1810.9 | Fire Mode Log: Event | 0
| 18110 | 1811 | Fire Mode Log: Time | 0 | s
|  | 1811.1 | Fire Mode Log: Time | 0 | s
|  | 1811.2 | Fire Mode Log: Time | 0 | s
|  | 1811.3 | Fire Mode Log: Time | 0 | s
|  | 1811.4 | Fire Mode Log: Time | 0 | s
|  | 1811.5 | Fire Mode Log: Time | 0 | s
|  | 1811.6 | Fire Mode Log: Time | 0 | s
|  | 1811.7 | Fire Mode Log: Time | 0 | s
|  | 1811.8 | Fire Mode Log: Time | 0 | s
|  | 1811.9 | Fire Mode Log: Time | 0 | s
| 18120 | 1812 | Fire Mode Log: Date and Time | 2005-01-01
|  | 1812.1 | Fire Mode Log: Date and Time | 2005-01-01
|  | 1812.2 | Fire Mode Log: Date and Time | 2005-01-01
|  | 1812.3 | Fire Mode Log: Date and Time | 2005-01-01
|  | 1812.4 | Fire Mode Log: Date and Time | 2005-01-01
|  | 1812.5 | Fire Mode Log: Date and Time | 2005-01-01
|  | 1812.6 | Fire Mode Log: Date and Time | 2005-01-01
|  | 1812.7 | Fire Mode Log: Date and Time | 2005-01-01
|  | 1812.8 | Fire Mode Log: Date and Time | 2005-01-01
|  | 1812.9 | Fire Mode Log: Date and Time | 2005-01-01
| 20000 | 2000 | Feedback 1 Source | Analog input 54
| 20010 | 2001 | Feedback 1 Conversion | Linear
| 20020 | 2002 | Feedback 1 Source Unit | %
| 20030 | 2003 | Feedback 2 Source | No function
| 20040 | 2004 | Feedback 2 Conversion | Linear
| 20050 | 2005 | Feedback 2 Source Unit | %
| 20060 | 2006 | Feedback 3 Source | No function
| 20070 | 2007 | Feedback 3 Conversion | Linear
| 20080 | 2008 | Feedback 3 Source Unit | %
| 20120 | 2012 | Reference/Feedback Unit | %
| 20130 | 2013 | Minimum Reference/Feedb. | 0 | %
| 20140 | 2014 | Maximum Reference/Feedb. | 100 | %
| 20200 | 2020 | Feedback Function | Minimum
| 20210 | 2021 | Setpoint 1 | 0 | %
| 20220 | 2022 | Setpoint 2 | 0 | %
| 20230 | 2023 | Setpoint 3 | 0 | %
| 20300 | 2030 | Refrigerant | R22
| 20310 | 2031 | User Defined Refrigerant A1 | 10
| 20320 | 2032 | User Defined Refrigerant A2 | -2250
| 20330 | 2033 | User Defined Refrigerant A3 | 250
| 20700 | 2070 | Closed Loop Type | Auto
| 20710 | 2071 | PID Performance | Normal
| 20720 | 2072 | PID Output Change | 0.1
| 20730 | 2073 | Minimum Feedback Level | -999999 | %
| 20740 | 2074 | Maximum Feedback Level | 999999 | %
| 20790 | 2079 | PID Autotuning | Disabled
| 20810 | 2081 | PID Normal/ Inverse Control | Normal
| 20820 | 2082 | PID Start Speed [RPM] | 0 | RPM
| 20830 | 2083 | PID Start Speed [Hz] | 0 | Hz
| 20840 | 2084 | On Reference Bandwidth | 5 | %
| 20910 | 2091 | PID Anti Windup | On
| 20930 | 2093 | PID Proportional Gain | 0.5
| 20940 | 2094 | PID Integral Time | 20 | s
| 20950 | 2095 | PID Differentiation Time | 0 | s
| 20960 | 2096 | PID Diff. Gain Limit | 5
| 21000 | 2100 | Closed Loop Type | Auto
| 21010 | 2101 | PID Performance | Normal
| 21020 | 2102 | PID Output Change | 0.1
| 21030 | 2103 | Minimum Feedback Level | -999999
| 21040 | 2104 | Maximum Feedback Level | 999999
| 21090 | 2109 | PID Autotuning | Disabled
| 21100 | 2110 | Ext. 1 Ref./Feedback Unit | %
| 21110 | 2111 | Ext. 1 Minimum Reference | 0 | %
| 21120 | 2112 | Ext. 1 Maximum Reference | 100 | %
| 21130 | 2113 | Ext. 1 Reference Source | No function
| 21140 | 2114 | Ext. 1 Feedback Source | No function
| 21150 | 2115 | Ext. 1 Setpoint | 0 | %
| 21170 | 2117 | Ext. 1 Reference [Unit] | 0 | %
| 21180 | 2118 | Ext. 1 Feedback [Unit] | 0 | %
| 21190 | 2119 | Ext. 1 Output [%] | 0 | %
| 21200 | 2120 | Ext. 1 Normal/Inverse Control | Normal
| 21210 | 2121 | Ext. 1 Proportional Gain | 0.01
| 21220 | 2122 | Ext. 1 Integral Time | 10000 | s
| 21230 | 2123 | Ext. 1 Differentation Time | 0 | s
| 21240 | 2124 | Ext. 1 Dif. Gain Limit | 5
| 21300 | 2130 | Ext. 2 Ref./Feedback Unit | %
| 21310 | 2131 | Ext. 2 Minimum Reference | 0 | %
| 21320 | 2132 | Ext. 2 Maximum Reference | 100 | %
| 21330 | 2133 | Ext. 2 Reference Source | No function
| 21340 | 2134 | Ext. 2 Feedback Source | No function
| 21350 | 2135 | Ext. 2 Setpoint | 0 | %
| 21370 | 2137 | Ext. 2 Reference [Unit] | 0 | %
| 21380 | 2138 | Ext. 2 Feedback [Unit] | 0 | %
| 21390 | 2139 | Ext. 2 Output [%] | 0 | %
| 21400 | 2140 | Ext. 2 Normal/Inverse Control | Normal
| 21410 | 2141 | Ext. 2 Proportional Gain | 0.01
| 21420 | 2142 | Ext. 2 Integral Time | 10000 | s
| 21430 | 2143 | Ext. 2 Differentation Time | 0 | s
| 21440 | 2144 | Ext. 2 Dif. Gain Limit | 5
| 21500 | 2150 | Ext. 3 Ref./Feedback Unit | %
| 21510 | 2151 | Ext. 3 Minimum Reference | 0 | %
| 21520 | 2152 | Ext. 3 Maximum Reference | 100 | %
| 21530 | 2153 | Ext. 3 Reference Source | No function
| 21540 | 2154 | Ext. 3 Feedback Source | No function
| 21550 | 2155 | Ext. 3 Setpoint | 0 | %
| 21570 | 2157 | Ext. 3 Reference [Unit] | 0 | %
| 21580 | 2158 | Ext. 3 Feedback [Unit] | 0 | %
| 21590 | 2159 | Ext. 3 Output [%] | 0 | %
| 21600 | 2160 | Ext. 3 Normal/Inverse Control | Normal
| 21610 | 2161 | Ext. 3 Proportional Gain | 0.01
| 21620 | 2162 | Ext. 3 Integral Time | 10000 | s
| 21630 | 2163 | Ext. 3 Differentation Time | 0 | s
| 21640 | 2164 | Ext. 3 Dif. Gain Limit | 5
| 22000 | 2200 | External Interlock Delay | 0 | s
| 22200 | 2220 | Low Power Auto Set-up | Off
| 22210 | 2221 | Low Power Detection | Disabled
| 22220 | 2222 | Low Speed Detection | Disabled
| 22230 | 2223 | No-Flow Function | Off
| 22240 | 2224 | No-Flow Delay | 10 | s
| 22260 | 2226 | Dry Pump Function | Off
| 22270 | 2227 | Dry Pump Delay | 10 | s
| 22300 | 2230 | No-Flow Power | 0 | kW
| 22310 | 2231 | Power Correction Factor | 100 | %
| 22320 | 2232 | Low Speed [RPM] | 0 | RPM
| 22330 | 2233 | Low Speed [Hz] | 0 | Hz
| 22340 | 2234 | Low Speed Power [kW] | 0 | kW
| 22350 | 2235 | Low Speed Power [HP] | 0 | hp
| 22360 | 2236 | High Speed [RPM] | 0 | RPM
| 22370 | 2237 | High Speed [Hz] | 0 | Hz
| 22380 | 2238 | High Speed Power [kW] | 0 | kW
| 22390 | 2239 | High Speed Power [HP] | 0 | hp
| 22400 | 2240 | Minimum Run Time | 10 | s
| 22410 | 2241 | Minimum Sleep Time | 10 | s
| 22420 | 2242 | Wake-up Speed [RPM] | 0 | RPM
| 22430 | 2243 | Wake-up Speed [Hz] | 0 | Hz
| 22440 | 2244 | Wake-up Ref./FB Difference | 10 | %
| 22450 | 2245 | Setpoint Boost | 0 | %
| 22460 | 2246 | Maximum Boost Time | 60 | s
| 22500 | 2250 | End of Curve Function | Off
| 22510 | 2251 | End of Curve Delay | 10 | s
| 22600 | 2260 | Broken Belt Function | Off
| 22610 | 2261 | Broken Belt Torque | 10 | %
| 22620 | 2262 | Broken Belt Delay | 10 | s
| 22750 | 2275 | Short Cycle Protection | Disabled
| 22760 | 2276 | Interval between Starts | 0 | s
| 22770 | 2277 | Minimum Run Time | 0 | s
| 22800 | 2280 | Flow Compensation | Disabled
| 22810 | 2281 | Square-linear Curve Approximation | 100 | %
| 22820 | 2282 | Work Point Calculation | Disabled
| 22830 | 2283 | Speed at No-Flow [RPM] | 0 | RPM
| 22840 | 2284 | Speed at No-Flow [Hz] | 0 | Hz
| 22850 | 2285 | Speed at Design Point [RPM] | 1500 | RPM
| 22860 | 2286 | Speed at Design Point [Hz] | 50 | Hz
| 22870 | 2287 | Pressure at No-Flow Speed | 0
| 22880 | 2288 | Pressure at Rated Speed | 999999.999
| 22890 | 2289 | Flow at Design Point | 0
| 22900 | 2290 | Flow at Rated Speed | 0
| 23000 | 2300 | ON Time | 0:00
|  | 2300.1 | ON Time | 0:00
|  | 2300.2 | ON Time | 0:00
|  | 2300.3 | ON Time | 0:00
|  | 2300.4 | ON Time | 0:00
|  | 2300.5 | ON Time | 0:00
|  | 2300.6 | ON Time | 0:00
|  | 2300.7 | ON Time | 0:00
|  | 2300.8 | ON Time | 0:00
|  | 2300.9 | ON Time | 0:00
| 23010 | 2301 | ON Action | Disabled
|  | 2301.1 | ON Action | Disabled
|  | 2301.2 | ON Action | Disabled
|  | 2301.3 | ON Action | Disabled
|  | 2301.4 | ON Action | Disabled
|  | 2301.5 | ON Action | Disabled
|  | 2301.6 | ON Action | Disabled
|  | 2301.7 | ON Action | Disabled
|  | 2301.8 | ON Action | Disabled
|  | 2301.9 | ON Action | Disabled
| 23020 | 2302 | OFF Time | 0:00
|  | 2302.1 | OFF Time | 0:00
|  | 2302.2 | OFF Time | 0:00
|  | 2302.3 | OFF Time | 0:00
|  | 2302.4 | OFF Time | 0:00
|  | 2302.5 | OFF Time | 0:00
|  | 2302.6 | OFF Time | 0:00
|  | 2302.7 | OFF Time | 0:00
|  | 2302.8 | OFF Time | 0:00
|  | 2302.9 | OFF Time | 0:00
| 23030 | 2303 | OFF Action | Disabled
|  | 2303.1 | OFF Action | Disabled
|  | 2303.2 | OFF Action | Disabled
|  | 2303.3 | OFF Action | Disabled
|  | 2303.4 | OFF Action | Disabled
|  | 2303.5 | OFF Action | Disabled
|  | 2303.6 | OFF Action | Disabled
|  | 2303.7 | OFF Action | Disabled
|  | 2303.8 | OFF Action | Disabled
|  | 2303.9 | OFF Action | Disabled
| 23040 | 2304 | Occurrence | All days
|  | 2304.1 | Occurrence | All days
|  | 2304.2 | Occurrence | All days
|  | 2304.3 | Occurrence | All days
|  | 2304.4 | Occurrence | All days
|  | 2304.5 | Occurrence | All days
|  | 2304.6 | Occurrence | All days
|  | 2304.7 | Occurrence | All days
|  | 2304.8 | Occurrence | All days
|  | 2304.9 | Occurrence | All days
| 23100 | 2310 | Maintenance Item | Motor bearings
|  | 2310.1 | Maintenance Item | Motor bearings
|  | 2310.2 | Maintenance Item | Motor bearings
|  | 2310.3 | Maintenance Item | Motor bearings
|  | 2310.4 | Maintenance Item | Motor bearings
|  | 2310.5 | Maintenance Item | Motor bearings
|  | 2310.6 | Maintenance Item | Motor bearings
|  | 2310.7 | Maintenance Item | Motor bearings
|  | 2310.8 | Maintenance Item | Motor bearings
|  | 2310.9 | Maintenance Item | Motor bearings
|  | 2310.1 | Maintenance Item | Motor bearings
|  | 2310.11 | Maintenance Item | Motor bearings
|  | 2310.12 | Maintenance Item | Motor bearings
|  | 2310.13 | Maintenance Item | Motor bearings
|  | 2310.14 | Maintenance Item | Motor bearings
|  | 2310.15 | Maintenance Item | Motor bearings
|  | 2310.16 | Maintenance Item | Motor bearings
|  | 2310.17 | Maintenance Item | Motor bearings
|  | 2310.18 | Maintenance Item | Motor bearings
|  | 2310.19 | Maintenance Item | Motor bearings
| 23110 | 2311 | Maintenance Action | Lubricate
|  | 2311.1 | Maintenance Action | Lubricate
|  | 2311.2 | Maintenance Action | Lubricate
|  | 2311.3 | Maintenance Action | Lubricate
|  | 2311.4 | Maintenance Action | Lubricate
|  | 2311.5 | Maintenance Action | Lubricate
|  | 2311.6 | Maintenance Action | Lubricate
|  | 2311.7 | Maintenance Action | Lubricate
|  | 2311.8 | Maintenance Action | Lubricate
|  | 2311.9 | Maintenance Action | Lubricate
|  | 2311.1 | Maintenance Action | Lubricate
|  | 2311.11 | Maintenance Action | Lubricate
|  | 2311.12 | Maintenance Action | Lubricate
|  | 2311.13 | Maintenance Action | Lubricate
|  | 2311.14 | Maintenance Action | Lubricate
|  | 2311.15 | Maintenance Action | Lubricate
|  | 2311.16 | Maintenance Action | Lubricate
|  | 2311.17 | Maintenance Action | Lubricate
|  | 2311.18 | Maintenance Action | Lubricate
|  | 2311.19 | Maintenance Action | Lubricate
| 23120 | 2312 | Maintenance Time Base | Disabled
|  | 2312.1 | Maintenance Time Base | Disabled
|  | 2312.2 | Maintenance Time Base | Disabled
|  | 2312.3 | Maintenance Time Base | Disabled
|  | 2312.4 | Maintenance Time Base | Disabled
|  | 2312.5 | Maintenance Time Base | Disabled
|  | 2312.6 | Maintenance Time Base | Disabled
|  | 2312.7 | Maintenance Time Base | Disabled
|  | 2312.8 | Maintenance Time Base | Disabled
|  | 2312.9 | Maintenance Time Base | Disabled
|  | 2312.1 | Maintenance Time Base | Disabled
|  | 2312.11 | Maintenance Time Base | Disabled
|  | 2312.12 | Maintenance Time Base | Disabled
|  | 2312.13 | Maintenance Time Base | Disabled
|  | 2312.14 | Maintenance Time Base | Disabled
|  | 2312.15 | Maintenance Time Base | Disabled
|  | 2312.16 | Maintenance Time Base | Disabled
|  | 2312.17 | Maintenance Time Base | Disabled
|  | 2312.18 | Maintenance Time Base | Disabled
|  | 2312.19 | Maintenance Time Base | Disabled
| 23130 | 2313 | Maintenance Time Interval | 1 | h
|  | 2313.1 | Maintenance Time Interval | 1 | h
|  | 2313.2 | Maintenance Time Interval | 1 | h
|  | 2313.3 | Maintenance Time Interval | 1 | h
|  | 2313.4 | Maintenance Time Interval | 1 | h
|  | 2313.5 | Maintenance Time Interval | 1 | h
|  | 2313.6 | Maintenance Time Interval | 1 | h
|  | 2313.7 | Maintenance Time Interval | 1 | h
|  | 2313.8 | Maintenance Time Interval | 1 | h
|  | 2313.9 | Maintenance Time Interval | 1 | h
|  | 2313.1 | Maintenance Time Interval | 1 | h
|  | 2313.11 | Maintenance Time Interval | 1 | h
|  | 2313.12 | Maintenance Time Interval | 1 | h
|  | 2313.13 | Maintenance Time Interval | 1 | h
|  | 2313.14 | Maintenance Time Interval | 1 | h
|  | 2313.15 | Maintenance Time Interval | 1 | h
|  | 2313.16 | Maintenance Time Interval | 1 | h
|  | 2313.17 | Maintenance Time Interval | 1 | h
|  | 2313.18 | Maintenance Time Interval | 1 | h
|  | 2313.19 | Maintenance Time Interval | 1 | h
| 23140 | 2314 | Maintenance Date and Time | 2006-01-01
|  | 2314.1 | Maintenance Date and Time | 2006-01-01
|  | 2314.2 | Maintenance Date and Time | 2006-01-01
|  | 2314.3 | Maintenance Date and Time | 2006-01-01
|  | 2314.4 | Maintenance Date and Time | 2006-01-01
|  | 2314.5 | Maintenance Date and Time | 2006-01-01
|  | 2314.6 | Maintenance Date and Time | 2006-01-01
|  | 2314.7 | Maintenance Date and Time | 2006-01-01
|  | 2314.8 | Maintenance Date and Time | 2006-01-01
|  | 2314.9 | Maintenance Date and Time | 2006-01-01
|  | 2314.1 | Maintenance Date and Time | 2006-01-01
|  | 2314.11 | Maintenance Date and Time | 2006-01-01
|  | 2314.12 | Maintenance Date and Time | 2006-01-01
|  | 2314.13 | Maintenance Date and Time | 2006-01-01
|  | 2314.14 | Maintenance Date and Time | 2006-01-01
|  | 2314.15 | Maintenance Date and Time | 2006-01-01
|  | 2314.16 | Maintenance Date and Time | 2006-01-01
|  | 2314.17 | Maintenance Date and Time | 2006-01-01
|  | 2314.18 | Maintenance Date and Time | 2006-01-01
|  | 2314.19 | Maintenance Date and Time | 2006-01-01
| 23150 | 2315 | Reset Maintenance Word | Do not reset
| 23160 | 2316 | Maintenance Text
|  | 2316.1 | Maintenance Text
|  | 2316.2 | Maintenance Text
|  | 2316.3 | Maintenance Text
|  | 2316.4 | Maintenance Text
|  | 2316.5 | Maintenance Text
| 23500 | 2350 | Energy Log Resolution | Last 24 Hours
| 23510 | 2351 | Period Start | 2006-01-01
| 23530 | 2353 | Energy Log | 0
|  | 2353.1 | Energy Log | 0
|  | 2353.2 | Energy Log | 0
|  | 2353.3 | Energy Log | 0
|  | 2353.4 | Energy Log | 0
|  | 2353.5 | Energy Log | 0
|  | 2353.6 | Energy Log | 0
|  | 2353.7 | Energy Log | 0
|  | 2353.8 | Energy Log | 0
|  | 2353.9 | Energy Log | 0
|  | 2353.1 | Energy Log | 0
|  | 2353.11 | Energy Log | 0
|  | 2353.12 | Energy Log | 0
|  | 2353.13 | Energy Log | 0
|  | 2353.14 | Energy Log | 0
|  | 2353.15 | Energy Log | 0
|  | 2353.16 | Energy Log | 0
|  | 2353.17 | Energy Log | 0
|  | 2353.18 | Energy Log | 0
|  | 2353.19 | Energy Log | 0
|  | 2353.2 | Energy Log | 0
|  | 2353.2 | Energy Log | 0
|  | 2353.21 | Energy Log | 0
|  | 2353.22 | Energy Log | 0
|  | 2353.23 | Energy Log | 0
|  | 2353.24 | Energy Log | 0
|  | 2353.25 | Energy Log | 0
|  | 2353.26 | Energy Log | 0
|  | 2353.27 | Energy Log | 0
|  | 2353.28 | Energy Log | 0
|  | 2353.29 | Energy Log | 0
|  | 2353.3 | Energy Log | 0
| 23600 | 2360 | Trend Variable | Power [kW]
| 23610 | 2361 | Continuous Bin Data | 0
|  | 2361.1 | Continuous Bin Data | 0
|  | 2361.2 | Continuous Bin Data | 0
|  | 2361.3 | Continuous Bin Data | 0
|  | 2361.4 | Continuous Bin Data | 0
|  | 2361.5 | Continuous Bin Data | 0
|  | 2361.6 | Continuous Bin Data | 0
|  | 2361.7 | Continuous Bin Data | 0
|  | 2361.8 | Continuous Bin Data | 0
|  | 2361.9 | Continuous Bin Data | 0
| 23620 | 2362 | Timed Bin Data | 0
|  | 2362.1 | Timed Bin Data | 0
|  | 2362.2 | Timed Bin Data | 0
|  | 2362.3 | Timed Bin Data | 0
|  | 2362.4 | Timed Bin Data | 0
|  | 2362.5 | Timed Bin Data | 0
|  | 2362.6 | Timed Bin Data | 0
|  | 2362.7 | Timed Bin Data | 0
|  | 2362.8 | Timed Bin Data | 0
|  | 2362.9 | Timed Bin Data | 0
| 23630 | 2363 | Timed Period Start | 2006-01-01
| 23640 | 2364 | Timed Period Stop | 2006-01-01
| 23650 | 2365 | Minimum Bin Value | 0 | %
|  | 2365.1 | Minimum Bin Value | 10 | %
|  | 2365.2 | Minimum Bin Value | 20 | %
|  | 2365.3 | Minimum Bin Value | 30 | %
|  | 2365.4 | Minimum Bin Value | 40 | %
|  | 2365.5 | Minimum Bin Value | 50 | %
|  | 2365.6 | Minimum Bin Value | 60 | %
|  | 2365.7 | Minimum Bin Value | 70 | %
|  | 2365.8 | Minimum Bin Value | 80 | %
|  | 2365.9 | Minimum Bin Value | 90 | %
| 23660 | 2366 | Reset Continuous Bin Data | Do not reset
| 23670 | 2367 | Reset Timed Bin Data | Do not reset
| 23800 | 2380 | Power Reference Factor | 100 | %
| 23810 | 2381 | Energy Cost | 1
| 23820 | 2382 | Investment | 0
| 23830 | 2383 | Energy Savings | 0 | kWh
| 23840 | 2384 | Cost Savings | 0
| 24000 | 2400 | Fire Mode Function | Disabled
| 24010 | 2401 | Fire Mode Configuration | Open Loop
| 24020 | 2402 | Fire Mode Unit | Hz
| 24030 | 2403 | Fire Mode Min Reference | 0 | Hz
| 24040 | 2404 | Fire Mode Max Reference | 50 | Hz
| 24050 | 2405 | Fire Mode Preset Reference | 0 | %
| 24060 | 2406 | Fire Mode Reference Source | No function
| 24070 | 2407 | Fire Mode Feedback Source | No function
| 24090 | 2409 | Fire Mode Alarm Handling | Trip, Critical Alarms
| 24100 | 2410 | Drive Bypass Function | Disabled
| 24110 | 2411 | Drive Bypass Delay Time | 0 | s
| 24900 | 2490 | Missing Motor Function | Off
| 24910 | 2491 | Missing Motor Coefficient 1 | 0
| 24920 | 2492 | Missing Motor Coefficient 2 | 0
| 24930 | 2493 | Missing Motor Coefficient 3 | 0
| 24940 | 2494 | Missing Motor Coefficient 4 | 0
| 24950 | 2495 | Locked Rotor Function | Off
| 24960 | 2496 | Locked Rotor Coefficient 1 | 0
| 24970 | 2497 | Locked Rotor Coefficient 2 | 0
| 24980 | 2498 | Locked Rotor Coefficient 3 | 0
| 24990 | 2499 | Locked Rotor Coefficient 4 | 0
| 25000 | 2500 | Cascade Controller | Disabled
| 25020 | 2502 | Motor Start | Direct on Line
| 25040 | 2504 | Pump Cycling | Disabled
| 25050 | 2505 | Fixed Lead Pump | Yes
| 25060 | 2506 | Number of Pumps | 2
| 25200 | 2520 | Staging Bandwidth | 10 | %
| 25210 | 2521 | Override Bandwidth | 100 | %
| 25220 | 2522 | Fixed Speed Bandwidth | 10 | %
| 25230 | 2523 | SBW Staging Delay | 15 | s
| 25240 | 2524 | SBW Destaging Delay | 15 | s
| 25250 | 2525 | OBW Time | 10 | s
| 25260 | 2526 | Destage At No-Flow | Disabled
| 25270 | 2527 | Stage Function | Enabled
| 25280 | 2528 | Stage Function Time | 15 | s
| 25290 | 2529 | Destage Function | Enabled
| 25300 | 2530 | Destage Function Time | 15 | s
| 25400 | 2540 | Ramp Down Delay | 10 | s
| 25410 | 2541 | Ramp Up Delay | 2 | s
| 25420 | 2542 | Staging Threshold | 90 | %
| 25430 | 2543 | Destaging Threshold | 50 | %
| 25440 | 2544 | Staging Speed [RPM] | 0 | RPM
| 25450 | 2545 | Staging Speed [Hz] | 0 | Hz
| 25460 | 2546 | Destaging Speed [RPM] | 0 | RPM
| 25470 | 2547 | Destaging Speed [Hz] | 0 | Hz
| 25500 | 2550 | Lead Pump Alternation | Off
| 25510 | 2551 | Alternation Event | External
| 25520 | 2552 | Alternation Time Interval | 24 | h
| 25530 | 2553 | Alternation Timer Value
| 25540 | 2554 | Alternation Predefined Time | 0:00
| 25550 | 2555 | Alternate if Load < 50% | Enabled
| 25560 | 2556 | Staging Mode at Alternation | Slow
| 25580 | 2558 | Run Next Pump Delay | 0.1 | s
| 25590 | 2559 | Run on Mains Delay | 0.5 | s
| 25800 | 2580 | Cascade Status
| 25810 | 2581 | Pump Status
| 25820 | 2582 | Lead Pump | 0
| 25830 | 2583 | Relay Status
|  | 2583.1 | Relay Status
|  | 2583.2 | Relay Status
|  | 2583.3 | Relay Status
|  | 2583.4 | Relay Status
|  | 2583.5 | Relay Status
|  | 2583.6 | Relay Status
|  | 2583.7 | Relay Status
|  | 2583.8 | Relay Status
| 25840 | 2584 | Pump ON Time | 0 | h
|  | 2584.1 | Pump ON Time | 0 | h
|  | 2584.2 | Pump ON Time | 0 | h
|  | 2584.3 | Pump ON Time | 0 | h
|  | 2584.4 | Pump ON Time | 0 | h
|  | 2584.5 | Pump ON Time | 0 | h
|  | 2584.6 | Pump ON Time | 0 | h
|  | 2584.7 | Pump ON Time | 0 | h
|  | 2584.8 | Pump ON Time | 0 | h
|  | 2584.9 | Pump ON Time | 0 | h
| 25850 | 2585 | Relay ON Time | 0 | h
|  | 2585.1 | Relay ON Time | 0 | h
|  | 2585.2 | Relay ON Time | 0 | h
|  | 2585.3 | Relay ON Time | 0 | h
|  | 2585.4 | Relay ON Time | 0 | h
|  | 2585.5 | Relay ON Time | 0 | h
|  | 2585.6 | Relay ON Time | 0 | h
|  | 2585.7 | Relay ON Time | 0 | h
|  | 2585.8 | Relay ON Time | 0 | h
| 25860 | 2586 | Reset Relay Counters | Do not reset
| 25900 | 2590 | Pump Interlock | Off
|  | 2590.1 | Pump Interlock | Off
|  | 2590.2 | Pump Interlock | Off
|  | 2590.3 | Pump Interlock | Off
|  | 2590.4 | Pump Interlock | Off
|  | 2590.5 | Pump Interlock | Off
|  | 2590.6 | Pump Interlock | Off
|  | 2590.7 | Pump Interlock | Off
|  | 2590.8 | Pump Interlock | Off
|  | 2590.9 | Pump Interlock | Off
| 25910 | 2591 | Manual Alternation | 0
| 50000 | x | Control Word (CTW) | 0
| 50010 | x | Bus Reference (MRV) | 0
| 50200 | x | Status Word (STW) | 0
| 50210 | x | Speed Output (MAV) | 0